## PTE Data
22246
LOTT Centrate Handling Facility Rehab
ORCAA PTE and TAP Analysis
Existing; ammonia
Parameter | Value | Unit | Notes
Avg. NH₃ gas level | 3.4 | ppm | Measured ambient ammonia
NH₃ molecular mass | 17.034 | g/mol | Periodic Table
Avg. NH₃ gas level | 2.3687 | mg/m³ | Conversion; assuming 25 °C and 1 atm
Avg. NH₃ gas level | 0.0023687 | mg/L | Conversion
Airflow | 20000 | cfm | Measured stack airflow
Airflow | 33980.2 | m³/hr | Conversion
Mass rate of NH₃ | 80490.1297 | mg/hr | Calculated
Mass rate of NH₃ | 0.08049 | kg/hr | Conversion
Mass rate of NH₃ | 0.17748 | lbm/hr | Conversion
Existing PTE NH₃ | 4.2595 | lbm/day | Conversion
Proposed; ammonia
Parameter | Value | Unit | Notes
Avg. NH₃ gas level | 3.4 | ppm | Measured ambient ammonia
NH₃ molecular mass | 17.034 | g/mol | Periodic Table
Avg. NH₃ gas level | 2.3687 | mg/m³ | Conversion; assuming 25 °C and 1 atm
Avg. NH₃ gas level | 0.0023687 | mg/L | Conversion
Airflow | 44000 | cfm | Proposed ventilation rate
Airflow | 74756.44 | m³/hr | Conversion
Mass rate of NH₃ | 177078.2853 | mg/hr | Calculated
Mass rate of NH₃ | 0.17708 | kg/hr | Conversion
Mass rate of NH₃ | 0.39046 | lbm/hr | Conversion
Proposed PTE NH₃ | 9.371 | lbm/day | Conversion
Increase in PTE NH₃ | 5.1114 | lbm/day
22246
LOTT Centrate Handling Facility Rehab
ORCAA PTE and TAP Analysis
Existing; Hydrogen sulfide
Parameter | Value | Unit | Notes
Avg. H₂S gas level | 1.8 | ppm | Measured ambient hydrogen sulfide
H₂S molecular mass | 34.1 | g/mol | Periodic Table
Avg. H₂S gas level | 2.5104 | mg/m³ | Conversion; assuming 25 °C and 1 atm
Avg. H₂S gas level | 0.0025104 | mg/L | Conversion
Airflow | 20000 | cfm | Measured stack airflow
Airflow | 33980.2 | m³/hr | Conversion
Mass rate of H₂S | 85304.8947 | mg/hr | Calculated
Mass rate of H₂S | 0.085305 | kg/hr | Conversion
Mass rate of H₂S | 0.1881 | lbm/hr | Conversion
Removal efficency | 0% |  | Efficiency of existing odor control equipment is unknown and assumed to be negligible
Existing PTE H₂S | 4.5143 | lbm/day | Conversion
Proposed; Hydrogen sulfide
Parameter | Value | Unit | Notes
Avg. H₂S gas level | 1.8 | ppm | Measured ambient hydrogen sulfide
H₂S molecular mass | 34.1 | g/mol | Periodic Table
Avg. H₂S gas level | 2.5104 | mg/m³ | Conversion; assuming 25 °C and 1 atm
Avg. H₂S gas level | 0.0025104 | mg/L | Conversion
Airflow | 44000 | cfm | Proposed ventilation rate
Airflow | 74756.44 | m³/hr | Conversion
Mass rate of H₂S | 187670.7684 | mg/hr | Calculated
Mass rate of H₂S | 0.18767 | kg/hr | Conversion
Mass rate of H₂S | 0.41381 | lbm/hr | Conversion
Removal efficency | 99% |  | Per basis of design filter equipment
Proposed PTE H₂S | 0.099315 | lbm/day | Conversion
Decrease in PTE NH₃ | -4.415 | lbm/day