## Instructions
FOR NOₓ AND CO READINGS
| Span Concentration | Concentration of the span gas used. It must fit within the 50/200 range as explained on the worksheet
| Pre-test Span | The reading with the span gas before you begin the tune-up
| Post-test Span | The reading with the span gas after you finish the tune-up
* | Pre-test Zero | The reading with ambient air before you begin the tune-up. This assumes that ambient air has neglible NOₓ or CO
* | Post-test Zero | The reading with ambient air after you finish the tune-up. This assumes that ambient air has neglible NOₓ or CO
The zero readings should be as close to zero as possible.
FOR OXYGEN READINGS
| Span Concentration | If your span gas contains oxygen, then enter it here. Otherwise, use ambeint air and a default value of 20.9
| Pre-test Span | The reading with ambient air before you begin the tune-up
| Post-test Span | The reading with ambient air after you finish the tune-up
* | Pre-test Zero | The reading with the span gas before you begin the tune-up. This assumes that your span gas has negligible O₂
* | Post-test Zero | The reading with the span gas after you finish the tune-up. This assumes that your span gas has negligible O₂
*The zero readings should be as close to zero as possible.
**Note on Oxygen Reading
The first row on the machine is the zero reading, not the span reading. The oxygen reading with ambient air should be 20.9.
Facility Permit Information
If you do not have the information from the facility, some facilities' permits can be found on the ORCAA website: https://www.orcaa.org/
Or call the facility representative at ORCAA: 360-539-7610
40 CFR 63 Subpart JJJJJJ (Boiler MACT) Monitoring Requirements for Liquid and Solid Fueled Boilers - Must be completed a minimum of every 2 years
This does not need to be performed or documented for natural gas only combustion units. If a unit is capable of firing a fuel other than natural gas then Subpart JJJJJJ applies.
Refer to the EPA website for more details on compliance at this address http://www.epa.gov/boilercompliance
Person performing the Subpart JJJJJJ inspection and certification should sign and date in the Test Notes box.
NOₓ and CO values should be recorded UNCORRECTED - NO auto 3% correction. The data sheet will provide O₂ correction as well as drift and zero correction.
Notes on Individual Fields on the Monitoring Data Sheet
| Facility Name | This is the name of the facility.
| ORCAA ID | This is the ORCAA assigned facility ID and is unique to every facility.
| Emission Unit ID | This is the ORCAA or facility name tag on the combustion unit - this will be identified in the ORCAA permit and/or by name tag on the unit - important to get this correct. This is NOT the L&I ID or Boiler inspector ID.
| Boiler manufacturer | This is the manufacturers name of the BOILER - not the burner
| Boiler Model Number | This is the BOILER manufacturers model number usually listed on the manufacturer applied name tag
| Boiler Serial Number | This is the manufacturers BOILER serial number usually listed on the manufacturer applied name tag
| Burner Manufacturer | This is the manufacturer of the BURNER - many times it is different than the boiler but not always
| Burner Model Number | This is the BURNER manufacturers model number usually listed on the manufacturer name tag on the BURNER
| Burner Serial Number | This is the BURNER manufacturers serial number usually listed on the manufacturer name tag on the BURNER
| Fuel Type | This cell has a Drop-Down menue of fuel types.
| Design Firing Rate | This data is usually found on the boiler name plate - if not there then it can be found in the ORCAA Technical Support Document (TSD) for the permit. The MMBtu/hr stands for million Btu per hour - use correct decimals.
| Tested Firing Rate | This field is sometimes difficult to fill in because there is usually no fuel meter. In this case indicate high fire or maximum or medium, etc
| Stack Temperature | This temperature is more important when firing rate is unknown - it many times provides an indication of firing rate and can be used to diagnose emission issues. ALWAYS record. It is auto generated on the form by filling in the individual temperatures as monitored.
| Time of Pre-Test Calibration |  | The monitoring procedure requires that pre and post calibrations be performed within 12 hours of each other - if not the data may be invalidated.
Time of Post-Test Calibration
Does the Permit/NOC have a NOₓ or CO Limit?
If yes note the permit/NOC number and limit in the boxes below the question. These limits are used to trigger WARNINGS in the WARNING BOX
If no, leave blank - self defeating if you do not enter numbers when the permit/NOC has limits. If there is a question call ORCAA.
In the Data box
| AS FOUND line | This is a single set of values for Temp, NOₓ, CO and O₂ - required only for Subpart JJJJJJ - can also be provided for other units - no adjustments should be made to the combustion unit before taking this reading.
The combustion unit should be warmed up and at high fire before taking this reading unles the unit has a permit condition specifying otherwise (e.g. some permits require 'normal operating load').
If the combustion unit is not within permit limits, adjustments should be made to bring the combusiton unit into compliance. Recheck as many times as needed to bring unit into compliance.
When the unit is capable of maintaining compliant emission levels, the final set of readings should be recorded on the log sheet - these data would be the AS LEFT condition and should reflect compliant levels.
If the unit can not be adjusted to achieve compliant emission levels, call ORCAA for guidance.
A minimum of 10 readings 30 seconds apart (5 minutes) is necessary to get a valid average test result. More data may be recorded if desired.
Combustion analyzer tapes should be printed and maintained for each combustion unit. The tapes should be annotated to indicate which run they coincide with and which combustion unit.
The recording strips (tapes) should be attached to a piece of paper and copied or scanned to be sent to ORCAA - the facility should maintain the original tapes.

## ORCAA Example
Olympic Region Clean Air Agency - Boiler Tune-Up Worksheet - O₂ Basis
| Facility Name: | XSPS Corporation |  |  | Date Performed: | 2023-07-31
General Instructions:
| Emission Unit Identifier/name: | Boiler #3 |  |  | 1. The boiler should be tuned-up at the load or firing rates recommended by your boiler manufacturer. If a manufacturer recommendation is not available, the boiler should be tuned-up at the load or firing rates your boiler typically operates at. Use a separate worksheet for each load level tested during your tune-up. 2. The CO and NOₓ span gas concentrations must not be less than 50% of the target/permitted pollutant concentration nor more than 200% of the target/permitted pollutant concentration. A lower concentration span gas may be used if it is more representative of measured concentrations. 3. The response check is failed if the difference between the pre-test and post-test readings is greater than 10% of the initial span value. 4. The calibration error check is failed if the pre-test analyzer response to a span or zero gas differs from the span or zero value by more than 10% of the span gas concentration. 5. No more than 12 hours may elapse between the pre-test and post-test analyzer response checks. 6. Calibration and use of an NO₂ cell is required, if: a. There are significant quantities of NO₂ expected (e.g., specific types of catalysts, afterburners, etc.), or b. The combustion analyzer does not have an integral or supplemental NO₂ to NO converter. 7. Include available documentation of monitoring and quality assurance results such as printouts ("tapes"), data log files, span gas cylinder calibrations, calculations, etc.
| Combust. Unit Manufacturer: | Acme Boiler
| Combust. Unit Model No: | Low Emissions 17
| Combust. Unit Serial No: | 57713
| Burner Manufacturer: | Global Burner
| Burner Model No: | Super Clean 17
| Burner Serial Number: | 12345
| Monitoring Company: | Bob's Boiler Service
| Analyst Name: | Bob Smith
| Test Instrument Make: | Combustion King
| Test Instrument Model: | CK-01
| Fuel Type: | Diesel
| Design Firing Rate: | 25.5 | MMBtu/hr
| Tested Firing Rate: | 20.8 | MMBtu/hr
|  | Time of Pre-Test Calibration: | 10:15
|  | Time of Post-Test Calibration: | 11:00
|  |  | Does the boiler have permit limits for CO and NOₓ? | Yes
Tune-Up Targets |  | NOX Target (ppm) | CO Target (ppm) | O₂ Correction (%) | 40 CFR 63 Subpart JJJJJJ (Boiler MACT) Monitoring Requirements for Liquid and Solid Fueled Boilers
Tune-Up Targets: |  |  |  | 3 | Was the burner inspected? |  |  | *
Source of Targets: |  | Manufacturer | Manufacturer | Manufacturer | Was the flame pattern inspected and optimized? |  |  | *
[5 empty] | Was the air-to-fuel ratio system operating properly? |  |  | *
Quality Assurance Results |  | NOX (ppm) | CO (ppm) | O₂ (%) | Were total CO emissions optimized? |  |  | *
| Span Concentration: | 101.2 | 55.6 | 20.9 | Describe any maintenance performed on the burner or boiler system in the "Test Notes" section.
| Pre-Test Span Reading: | 95 | 54 | 20.9
| Post-Test Span Reading: | 93 | 52 | 20.8
| Pre-Test Zero Reading: | -0.1 | 0 | 0 | Test Notes (including a description of any adjustments made):
| Post-Test Zero Reading: | 0 | 0.2 | 0.1
Results (Record at least once every 30 seconds for 5 minutes)
Sample | Stack Temp (°F) | NOX Reading (ppm) | CO Reading (ppm) | O₂ Reading (%)
As Found | 341 | 45 | 20 | 2.3
1 | 324 | 29 | 13 | 3
2 | 324 | 28 | 12 | 3.1
3 | 324 | 27 | 13 | 3
4 | 324 | 27 | 14 | 3
5 | 324 | 27 | 15 | 2.9
6 | 324 | 26 | 13 | 3 | NOTIFICATIONS:
7 | 324 | 30 | 13 | 3 | No Issues Identified. Please remember to include the analyzer printouts and the calibration gas certificates with your submittal.
8 | 324 | 28 | 13 | 3
9 | 324 | 28 | 12 | 3
10 | 324 | 28 | 11 | 3
11
12
13
14
15
16
17
18
19
20
Test Averages: | 324 | 27.8 | 12.9 | 3
Drift Corrected Values: |  | 29.9673 | 13.4533 | 2.9642
Oxygen Corrected Values: |  | 29.9074 | 13.4264
Rev. 06/27/2023
Questions? - Call the Olympic Region Clean Air Agency at 360-539-7610
Note on B43: Record the values found before any adjustments, maintenance, or tuning is conducted.

## Monitoring Data Sheet
Olympic Region Clean Air Agency - Boiler Tune-Up Worksheet - O₂ Basis
| Facility Name: |  |  |  | Date Performed:
General Instructions:
| Emission Unit Identifier/name: |  |  |  | 1. The boiler should be tuned-up at the load or firing rates recommended by your boiler manufacturer. If a manufacturer recommendation is not available, the boiler should be tuned-up at the load or firing rates your boiler typically operates at. Use a separate worksheet for each load level tested during your tune-up. 2. The CO and NOₓ span gas concentrations must not be less than 50% of the target/permitted pollutant concentration nor more than 200% of the target/permitted pollutant concentration. A lower concentration span gas may be used if it is more representative of measured concentrations. 3. The response check is failed if the difference between the pre-test and post-test readings is greater than 10% of the initial span value. 4. The calibration error check is failed if the pre-test analyzer response to a span or zero gas differs from the span or zero value by more than 10% of the span gas concentration. 5. No more than 12 hours may elapse between the pre-test and post-test analyzer response checks. 6. Calibration and use of an NO₂ cell is required, if: a. There are significant quantities of NO₂ expected (e.g., specific types of catalysts, afterburners, etc.), or b. The combustion analyzer does not have an integral or supplemental NO₂ to NO converter. 7. Include available documentation of monitoring and quality assurance results such as printouts ("tapes"), data log files, span gas cylinder calibrations, calculations, etc.
Combust. Unit Manufacturer:
Combust. Unit Model No:
Combust. Unit Serial No:
Burner Manufacturer:
Burner Model No:
Burner Serial Number:
Monitoring Company:
Analyst Name:
Test Instrument Make:
Test Instrument Model:
Fuel Type:
| Design Firing Rate: |  | MMBtu/hr
| Tested Firing Rate: |  | MMBtu/hr
Time of Pre-Test Calibration:
Time of Post-Test Calibration:
Is the unit subject to any limits for CO and NOₓ?
Tune-Up Targets |  | NOX Target (ppm) | CO Target (ppm) | O₂ Correction (%) | 40 CFR 63 Subpart JJJJJJ (Boiler MACT) Monitoring Requirements for Liquid and Solid Fueled Boilers
Tune-Up Targets: |  |  |  |  | Was the burner inspected? (yes/no) |  | *
Source of Targets: |  |  |  |  | Was the flame pattern inspected and optimized? (yes/no) |  | *
[5 empty] | Was the air-to-fuel ratio system operating properly? (yes/no) |  | *
Quality Assurance Results |  | NOX (ppm) | CO (ppm) | O₂ (%) | Were total CO emissions optimized? (yes/no) |  | *
| Span Concentration: |  |  |  | Describe any maintenance performed on the burner or boiler system in the "Test Notes" section.
Pre-Test Span Reading:
Post-Test Span Reading:
| Pre-Test Zero Reading: |  |  |  | Test Notes (including a description of any adjustments made):
Post-Test Zero Reading:
Results (Record at least once every 30 seconds for 5 minutes)
Sample | Stack Temp (°F) | NOX Reading (ppm) | CO Reading (ppm) | O₂ Reading (%)
As Found
1
2
3
4
5
6 |  |  |  |  | NOTIFICATIONS:
7
8
9
10
11
12
13
14
15
16
17
18
19
20
Test Averages: | No Data | No Data | No Data | No Data
Drift Corrected Values: |  | No Span | No Span | No Span
Oxygen Corrected Values: |  | No Span | No Span
Rev. 06/27/2023
Questions? - Call the Olympic Region Clean Air Agency at 360-539-7610
Note on B43: Record the values found before any adjustments, maintenance, or tuning is conducted.

## Messages
Fail Conditions and Messages
Test # | Condition 1=Fail 0=Pass | Message | FAILURE MESSAGES |  |  | Fuel Types | F-factor | Sort |  | Responses
1 | 0 | • Cell D35 - NOₓ span concentration out of range - see note 1 above - NOₓ results invalid | [6 empty] | <-intentionally left blank |  | <-intentionally left blank
2 | 0 | • Cell E35 - CO span concentration out of range - see note 1 above - CO results invalid |  |  |  | Natural gas | 8710 | 1 |  | Yes
3 | 0 | • Cells D36 & D37 - NOₓ span drift excessive - see note 2 above - NOₓ results invalid |  |  |  | LPG | 8710 | 2 |  | No
4 | 0 | • Cells D38 & D39 - NOₓ zero drift excessive - see note 2 above - NOₓ results invalid |  |  |  | Diesel | 9190 | 3
5 | 0 | • Cells E36 & E37 - CO span drift excessive - see note 2 above - CO results invalid |  |  |  | Fuel Oil No 6 | 9190 | 4
6 | 0 | • Cells E38 & E39 - CO zero drift excessive - see note 2 above - CO results invalid |  |  |  | Alder bark dust | 8611 | 5 |  | Permit Limits? | 0
7 | 0 | • Cells F36 & F37 - O₂ span drift excessive - see note 2 above - O₂ results invalid |  |  |  | Bark | 9600 | 5
8 | 0 | • Cells F38 & F39 - O₂ zero drift excessive - see note 2 above - O₂ results invalid |  |  |  | Coal | 9780 | 5
9 | 0 | • Cell D36 - NOₓ pre-test span reading too high or too low - see note 3 above - NOₓ results invalid |  |  |  | Digester gas | 9450 | 5
10 | 0 | • Cell E36 - CO pre-test span reading too high or too low - see note 3 above - CO results invalid |  |  |  | Gasoline | 9190 | 5
11 | 0 | • Cell F36 - O₂ pre-test span reading too high or too low - see note 3 above - O₂ results invalid |  | Total Fail Messages: | 0 | Hogged fuel | 9600 | 5
12 | 0 | • Cell D38 - NOₓ pre-test zero reading too high or too low - see note 3 above - NOₓ results invalid |  |  |  | Landfill gas | 9450 | 5
13 | 0 | • Cell E38 - CO pre-test zero reading too high or too low - see note 3 above - CO results invalid |  |  |  | LNG | 8710 | 5
14 | 0 | • Cell F38 - O₂ pre-test zero reading too high or too low - see note 3 above - O₂ results invalid |  |  |  | Methane | 8710 | 5
15 | 0 | • Cell F30 - No O₂ correction value has been entered. Enter appropriate O₂ correction value |  |  |  | Butane | 8710 | 5
16 | 0 | • Measured NOₓ exceeds tune-up target |  |  |  | Process gas | 9450 | 5
17 | 0 | • Measured CO exceeds tune-up target |  |  |  | Propane | 8710 | 5
18 | 0 | • Cell D30 - No NOₓ limit entered |  |  |  | PS300 | 9190 | 5
19 | 0 | • Cell E30 - No CO limit entered |  |  |  | Sander dust | 9240 | 5
20 | 0 | • Cell E30 - NOₓ limit inconsistent with answer in F25 |  |  |  | Wood waste | 9240 | 5
21 | 0 | • Cell E30 - CO limit inconsistent with answer in F25 |  |  |  | Wood waste and sander dust | 9240 | 5
22 | 0 | • Cell F38 - Pre-Test O₂ zero appears to be too high. Assure correct value was entered |  |  |  | Wood/Gas | 9000 | 5
23 | 0 | • Cell F36 - Post-Test O₂ zero appears to be too high. Assure correct value was entered
24 | 0 | • Cell F30 - Check permit for proper O₂ correction, zero is probably not correct
25 | 0 | • Cell F30 - You must enter an O₂ correction, even if you have no permit limit; default for natural gas is 3%.
26 | 0 | • Cell F35 - O₂ span should be either ambient (20.9) or the value of a non-zero O₂ calibration gas
27 | 0 | • Cell F38 - O₂ zero should be determined using your calibration gas (assuming there is no O₂)
28 | 0 | • Temperature data points entered below minimum. Only 0 data point entered.
29 | 0 | • NOₓ data points entered below minimum. Only 0 data point entered.
30 | 0 | • CO data points entered below minimum. Only 0 data point entered.
31 | 0 | • O₂ data points entered below minimum. Only 0 data point entered.
32 | 0 | • Be sure to select whether a permit limit exists or not in Cell F26
33
34
35
36
37
38
39
40